NUCLEAR ENERGY TECHNOLOGIES DESIGN COMPETITION

DETAILED DESIGN

FINAL EVALUATION REPORT

Team Name: NUClearly

Application ID: 5300592

Team ID: 995912

Category Name: Base Category - Detailed Design

Team Type: School Team

2026

DETAILED DESIGN

FINAL EVALUATION REPORT (FER)

Participants must mark the category they applied for and team type .

Only one option must be marked in each table below. More than one selection will not be accepted.

| MAIN CATEGORY |  |
| --- | --- |
| Detailed Design - 40 MWe Modular PWR |  |

TEAM TYPE

| Professional Team |  |
| --- | --- |
| School Team | ■ |

CONTENTS

TABLES	4

FIGURES	4

ABBREVIATIONS	4

1. PROJECT ABSTRACT / SCOPE OF THE PROJECT	5

1.1.	Project Abstract	5

1.2.	Scope of the Project	5

2. TEAM INTRODUCTION	5

3. LITERATURE REVIEW	6

4. METHODOLOGY AND FEASIBILTY	7

4.1.	Methodology	7

4.2.	Feasibilty	7

5. ORIGINALITY, INNOVATION AND DOMESTICITY OF THE PROJECT	8

5.1. Originality/Innovative Aspects	8

5.2. Domesticity Aspects	8

6. PROJECT WORK PLAN	8

7. BROADER IMPACTS AND TARGET AUDIENCE	8

8. MAIN PROJECT TITLES	9

8.1. Design Preparation Phase and General Description of the Plant	9

8.1.1 Plant and power	9

8.1.2 Primary system and thermal-hydraulics	10

8.1.3 Fuel and core	10

8.1.4 Engineered safety features and probabilistic targets	11

8.1.5 Outage schedule and derived relations	12

8.1.6 Design-preparation phase, methodology and basis documents	12

8.1.7 Design codes and standards	13

8.1.8 Reference regulatory and nuclear-safety requirements	14

8.2. Core Design	15

8.3. Fuel and Material Design	16

8.4. Cooling Circuit System Design	16

8.5. Safety Criteria	16

8.6. Reactor Safety Systems Design	17

8.7. Instrumentation and Control System Design	18

8.8. Auxiliary Systems Design	18

8.9. Energy Cycle and Integrated Systems	19

8.10. Plant Layout Design	19

8.11. Nuclear Waste Management	19

8.12. Economic Evaluation	20

REFERENCES	21

APPENDICES	21

TABLES

FIGURES

List of figures must be added

ABBREVIATIONS

Abbreviations must be added

1. PROJECT ABSTRACT / SCOPE OF THE PROJECT

1.1.	Project Abstract

Aegis-40 is a 40 MWe / 125 MWth integral pressurised-water small modular reactor designed for the TEKNOFEST 2026 Nuclear Energy Technologies Detailed Design category. The reactor is soluble-boron-free during normal operation and uses integral burnable absorbers and control rods for reactivity control. The primary system, including the core, once-through steam generator, self-pressuriser, and control-rod drives, is contained inside a single reactor pressure vessel. Natural circulation is used for the primary coolant, so reactor coolant pumps and large-bore primary piping are eliminated. The design combines electricity production with district heat through thermochemical energy storage and off-peak hydrogen production.

The report presents the design basis, core design, fuel and materials, thermal-hydraulic cooling circuit, safety criteria, reactor safety systems, instrumentation and control, auxiliary systems, energy cycle, plant layout, waste management, economic evaluation, and the digital appendix verification and validation plan. Figure placeholders are intentionally retained so that the team can insert its final drawings, flow diagrams, and analysis figures.

1.2.	Scope of the Project

The project scope corresponds to the Detailed Design - 40 MWe Modular PWR category. The design includes technical calculations, engineering analyses, component specifications, safety provisions, integrated systems, nuclear waste management, economic assessment, and a digital appendix plan for sample input files, reproducibility, repeatability, benchmarking, and verification against reliable sources. The content under Section 8 follows the official FER technical headings for the detailed-design category.

2. TEAM INTRODUCTION

The report is prepared by a multidisciplinary reactor design team organised by technical work packages rather than by personal identifiers. To comply with the template requirement, names, photographs, universities, institutions, and other personal information are not included.

| Team function | Contribution |
| --- | --- |
| Core and neutronics group | OpenMC core geometry, depletion, reactivity coefficients, peaking factors, shutdown margin, and spent-fuel inventory. |
| Thermal-hydraulics group | Natural-circulation loop balance, conjugate CFD, DNBR, peak clad temperature, and primary/secondary heat-transfer interfaces. |
| Fuel and materials group | Fuel-rod thermal stack, cladding and structural materials, irradiation behaviour, shielding materials, and front-end material compatibility. |
| Safety and PRA group | Deterministic safety criteria, accident prevention, passive safety systems, event-tree/fault-tree logic, and projected CDF/LRF framework. |
| I&C and auxiliary systems group | Reactor protection, ESFAS, diverse actuation, control-room concept, auxiliary systems, electrical systems, HVAC, fire protection, and radiation monitoring. |
| Energy-cycle and layout group | Rankine cycle, TCES, hydrogen interface, seawater heat sink, plant layout, critical piping, and constructability interfaces. |
| Waste and economics group | Waste intensity, spent-fuel storage criticality, secondary waste minimisation, LCOE, fuel-cycle cost, and comparison with reference reactors. |

3. LITERATURE REVIEW

Integral PWR small modular reactors provide the main architectural reference for Aegis-40 because they place the primary components inside the reactor pressure vessel and reduce large external primary piping. The design is anchored to published integral-PWR practice and the NuScale-class 37-assembly, 17×17, approximately 2 m active-height core envelope, while intentionally departing from soluble-boron chemical shim through the solid absorber strategy described in Section 8.2.

CAREM-25 is also used as one of the main reference designs for the overall plant concept, CAD development, reactor-building arrangement, containment philosophy, and passive safety-system layout. As an integral PWR SMR, CAREM provides a relevant engineering precedent for compact reactor-building organization, in-vessel primary-system integration, natural-circulation cooling, passive residual-heat-removal philosophy, emergency cooling arrangements, and simplified safety-system architecture. In Aegis-40, these CAREM-related references are not copied directly; instead, they are used as a comparative design basis for developing the reactor building, auxiliary-system placement, safety-system separation, passive heat-removal routes, and layout constraints suitable for a 40 MWe modular PWR.

Soluble-boron-free and burnable-absorber-controlled PWR studies support the project reactivity-control approach. The literature cited in the report includes work on SBF small PWRs, gadolinia depletion behaviour, erbia hold-down, and SMART/ATOM/PRATIC burnable-absorber zoning approaches. These studies are used to justify the division of power shaping between ring-zoned Gd₂O₃, intra-assembly enrichment grading, Er₂O₃ hold-down, and control-rod shutdown capability.

The thermal-hydraulic methodology is based on accepted nuclear heat-transfer and water-property references, including IAPWS-IF97, W-3 CHF methods, Jens-Lottes subcooled-boiling treatment, ANS-5.1 decay heat, and ASME V&V-20 grid-convergence practice. The waste, source-term, burnup-credit, and economics methodology is aligned with OECD-NEA, IAEA, NRC, and published LWR fuel-cycle references listed in the References section.

4. METHODOLOGY AND FEASIBILTY

4.1.	Methodology

The project methodology is an integrated design chain in which each discipline produces controlled design inputs for the next. Neutronic calculations establish core geometry, reactivity behaviour, depletion, and power distributions. Thermal-hydraulic analyses use those power distributions to size the natural-circulation loop and demonstrate heat-removal margins. Fuel-performance calculations evaluate centreline temperature, fission-gas release, rod pressure, cladding integrity, and material compatibility. Safety analysis then maps the design to deterministic criteria, passive safety systems, and probabilistic class targets. Energy-conversion, layout, waste-management, and economic analyses close the plant-level feasibility case.

The analysis toolchain includes OpenMC for neutron transport, depletion, shielding, and criticality; OpenFOAM-based conjugate CFD and correlation post-processing for hot-channel fuel/clad/coolant analysis; IAPWS-IF97 for water and steam properties; ANS-5.1 for decay heat; and purpose-built scripts for natural circulation, Rankine-cycle performance, exergy, waste, storage criticality, and economics. The mandatory digital appendix contains the sample input files and V&V plan for these codes.

4.2.	Feasibilty

The design is feasible within current nuclear engineering practice because it deliberately uses qualified LWR fuel geometry, conventional UO2/Zircaloy-4 fuel technology, an integral PWR architecture, passive heat removal, and a regenerative Rankine cycle. The principal feasibility advantage is the reduction of active primary equipment and large primary pipework through natural circulation and integral arrangement.

5. ORIGINALITY, INNOVATION AND DOMESTICITY OF THE PROJECT

5.1. Originality/Innovative Aspects

The original design contribution is the combination of a soluble-boron-free iPWR core, natural-circulation primary heat removal, passive safety systems, and polygeneration through thermochemical energy storage and off-peak hydrogen. The soluble-boron-free strategy removes the chemical-shim system and the boron-dilution accident path, while reactivity hold-down is transferred to solid Gd2O3 and Er2O3 burnable absorbers and control rods.

The design also integrates load-following through the secondary-side TCES buffer rather than deep reactor power manoeuvring. This protects the core from unnecessary xenon, peaking, and thermal-hydraulic perturbations while still supporting grid and district-heating flexibility. The digital twin is non-safety and read-only, allowing anomaly detection and maintenance support without compromising Class 1E protection independence.

5.2. Domesticity Aspects

The project supports Turkiye's nuclear technology development by using a Sinop Black Sea coastal siting concept, once-through seawater heat rejection, district-heating capability, hydrogen co-generation, and modular construction suited to local industrial participation. The design framework uses the Nukleer Duzenleme Kurumu regulatory environment together with IAEA and international standards, enabling a pathway for national capability building in reactor design, analysis, manufacturing, siting, safety assessment, and non-electric nuclear applications.

6. PROJECT WORK PLAN

The  work packages of the project with their sub-tasks throughout the whole project development timeline (from startup to loading of Final Evaluation Report to the system) must be given clearly (e.g. analyses, computer codes). The work plan of the project must be provided in a table with a weekly/monthly schedule.

7. BROADER IMPACTS AND TARGET AUDIENCE

7.1. Broader Impacts: In case of realization of the project, potential contributions  to Türkiye’s economy, social welfare and scientific knowledge must be detailed. A clear explanation on how the public can benefit from the expected outcomes of the project must be given.

7.2. Target Audience: Target audience of the project must be stated and how the project aligns with their needs must be explained clearly.

8. MAIN PROJECT TITLES

The following sections present the detailed 40 MWe modular PWR design under the official FER technical headings. Tables provide the design-basis quantities, materials, dimensions, standards, capacities, and analysis outputs that support the technical specifications. Figure placeholders are retained at the locations where the team can insert the final drawings and plots.

8.1. Design Preparation Phase and General Description of the Plant

The Aegis-40 is an integral, soluble-boron-free pressurised-water small modular reactor (iPWR-SMR) rated 125 MWth / 40 MWe net (32.0 % nameplate net efficiency). All primary equipment — core, helical-coil once-through steam generator, self-pressuriser and the control-rod drives — is housed within a single reactor pressure vessel (RPV); the primary coolant moves by natural circulation (no reactor coolant pumps). The plant is designed for a 60-year life, a small (~0.5 km) emergency-planning zone enabled by passive safety, factory-modular construction, and polygeneration (electricity + district heat via thermochemical storage + off-peak hydrogen). The candidate site is the Sinop Black-Sea coast (once-through seawater ultimate heat sink).

The two defining design choices are (i) operation without soluble boron, which removes the chemical-shim system and its boron-dilution accident pathway and transfers reactivity hold-down to solid burnable absorbers (Gd₂O₃ + Er₂O₃) and control rods, and (ii) the integral natural-circulation architecture, which eliminates large-bore primary piping and the reactor coolant pumps and so design-eliminates the large-break LOCA, the rod-ejection and the surge-line-break accident classes (§8.6.1).

8.1.1 Plant and power

Table 8.1-1

| Parameter | Value | Unit / note |
| --- | --- | --- |
| Plant type | Integral PWR (iPWR), soluble-boron-free | — |
| Thermal power | 125 | MWth |
| Net electrical output | 40 | MWe (net to grid) |
| Net thermal efficiency | 32.0 (nameplate) / 31.8 (computed, §8.9) | % |
| Design lifetime | 60 | years |
| Capacity factor — design target | 95 | % |
| Capacity factor | 90 | % (conservative) |
| Non-electric output | district heat (TCES) + off-peak H2 | §8.9 |
| Available process-heat temperature | 100–260 (flexible) | °C |
| Modular design | Yes | factory-fabricated |
| Construction duration (n-th unit) | < 30 | months (first concrete → criticality) |
| Emergency planning zone (radius) | 0.5 | km (design goal; closed by dose case §8.5) |
| Seismic design (SSE) | 0.3 | g (Safe-Shutdown Earthquake) |

8.1.2 Primary system and thermal-hydraulics

Table 8.1-2

| Parameter | Value | Unit / note |
| --- | --- | --- |
| Primary operating pressure | 12.8 | MPa (iPWR) |
| Primary design pressure (110 %) | ≈ 14.1 | MPa |
| Core inlet / outlet temperature | 258 / 308 | °C / °C |
| Core temperature rise ΔT | 50 | K |
| Core average temperature | 283 | °C |
| Saturation temp. @ 12.8 MPa | ≈ 331 | °C (→ ≈ 23 °C hot-leg subcooling) |
| Average primary mass flow | ≈ 467 | kg/s (G ≈ 543 kg/m²·s; natural circulation) |
| Natural-circulation thermal centre height H_tc | ≈ 4.0 | m (core-mid → OTSG-mid; §8.4 CFD loop balance) |
| Primary driving head | ≈ 3.67 | kPa (buoyancy at H_tc 4 m) |
| Primary coolant inventory | ≈ 26 (≈ 35 m³) | t [CONFIRM vs §8.4 T-H model] |
| Steam-generator (secondary) pressure | 4.5 | MPa |
| Steam temperature (OTSG outlet) | 296 | °C |
| Circulation mode | Natural circulation (no primary pumps) | — |

8.1.3 Fuel and core

Table 8.1-3

| Parameter | Value | Unit / note |
| --- | --- | --- |
| Number of fuel assemblies | 37 | 7×7 octagon (rows 3-5-7-7-7-5-3) |
| Lattice | 17×17 Westinghouse-type | 264 fuel + 24 guide + 1 instrument |
| Active core height | 200 | cm (+ 30 cm H₂O axial reflector each end) |
| Equivalent core diameter | ≈ 1483 | mm (across-flats 1512) |
| Heavy-metal loading (fresh) | 9.87 | tHM |
| Specific power | 12.66 | MW/tHM |
| Fuel material | UO₂ | enrichment-zoned |
| Enrichment (intra-FA grade: interior/mid/periphery) | 4.95 / 4.70 / 4.40 | wt% ²³⁵U |
| Enrichment (reflector-facing edge pins) | 4.0 | wt% (edge-pin de-rate) |
| Cladding | Zircaloy-4 (Zr-4) | - |
| Primary burnable absorber | Gd₂O₃ 6 wt%, ring-zoned (avg 20 rods/FA) | rings 1/8/16/12, weights 1.65/1.45/0.95/0.68 |
| Secondary burnable absorber | Er₂O₃ 0.75 wt% (16 rods/FA) | slow hold-down + cold SDM |
| Reload scheme | 4-batch | once-through |
| Control-rod clusters (CRA) | 16 | checkerboard; central FA = instrument; in-vessel CRDM |
| Control-rod absorber | B₄C (/ Ag-In-Cd or Hf) | [CONFIRM §8.6] |
| Cycle length |  | EFPD |
| Discharge burnup |  | GWd/MTU |
| Fuel reprocessing | None (once-through) | — |

8.1.4 Engineered safety features and probabilistic targets

Table 8.1-4 - These rows summarize §8.5–§8.7; values are reproduced here for the front page and are authoritative in those sections.

| System / metric | Value | Note |
| --- | --- | --- |
| Reactor shutdown systems | 2 diverse | (1) gravity-drop control rods; (2) passive Emergency Boron Injection (EBIS), dormant in normal operation (§8.6.2a) |
| Passive residual heat removal (PRHR) | 2 × 100 % | natural circulation to in-containment tank |
| Emergency feedwater (EFW) | gravity-driven | fail-open, no pumps |
| Passive containment cooling | 3 trains | continuously in service |
| Passive safety injection | gravity feed from IRWST | low-pressure coincidence |
| Containment | Dry steel-lined | Ø ≈ 15 m; design pressure ≈ 0.414 MPa [ANALYSIS-PENDING P/T] |
| Emergency power | 2 × EDG + 1E batteries | monitoring/backup only — core cooling is passive |
| Safety grace period (no AC, no seawater, no operator) | ≥ 72 h (target unlimited) | passive UHS = IRWST |
| Core Damage Frequency (CDF) | < 1×10⁻⁷ /ry (projected class target) | LOHS ≈ 1e-8, SBO ≈ 1e-11 demonstrated (§8.6.3) |
| Large Release Frequency (LRF) | < 1×10⁻⁸ /ry (projected class target) | — |

8.1.5 Outage schedule and derived relations

Major outages: 15 days every 12 months (refuelling) + 30 days every 120 months (turbine / vessel in-service inspection) → planned availability ≈ 95 %, consistent with the design CF. Derived: net efficiency = 40/125 = 32.0 %; specific power = 125/9.87 = 12.66 MW/tHM; primary flow from Q = ṁ·c_p·ΔT (c_p ≈ 5.35 kJ/kg·K @ 283 °C/12.8 MPa, IAPWS-IF97) → ṁ ≈ 467 kg/s (core mass flux G ≈ 543 kg/m²·s).

8.1.6 Design-preparation phase, methodology and basis documents

The parameter set above is the controlled output of the preliminary (conceptual/basic) design phase, developed through an integrated, reproducible analysis chain (IAEA SSG-52 §2; GSR Part 4 design-input control). Each domain produced a version-controlled basis document that becomes a verified input to detailed design.

Table 8.1-6 — Preliminary-design analyses and basis documents

| Design domain | Method / tool | Controlled output |
| --- | --- | --- |
| Neutronics, depletion, reactivity coefficients | OpenMC Monte-Carlo (ENDF/B-VIII.0), 37-FA 3-D core + depletion | aegis40_neutronics_FER.ipynb; §8.2 |
| Fuel performance (T_cl, FGR, rod pressure) | Steady-state fuel-rod conduction stack vs SSG-52 limits | §8.3 |
| Primary thermal-hydraulics | Natural-circulation loop balance + DNBR (IAPWS-IF97) | §8.4 (natcirc_primary.py) |
| Secondary power conversion | Regenerative Rankine + exergy (IAPWS-IF97) | §8.9 (thermo_cycle.py, thermo_exergy.py) |
| Shielding / dose | Coupled n-γ transport + ICRP-116 flux-to-dose | §8.2.6 (…_shielding_rev7.ipynb) |
| Waste / source term | Depletion inventory + ANSI/ANS-5.1 decay heat | §8.11 (src/aegis40/back_end) |
| Safety / PRA | Deterministic DBA + event/fault trees | §8.5/§8.6 (safety/) |
| Geometry / layout | Parametric CAD (RPV, assembly, pin, site STEP) | cad/, §8.10 |

8.1.7 Design codes and standards

Table 8.1-7

| Design domain | Code / standard | Application |
| --- | --- | --- |
| Class-1 nuclear pressure boundary | ASME BPVC Section III, Div. 1 (NB / NG) | RPV, OTSG, self-pressuriser, in-vessel CRDM, core support (§8.4) |
| Non-nuclear pressure parts / BOP | ASME BPVC Section VIII; ASME B31.1 | Condenser, feedwater heaters, secondary piping (§8.9) |
| Pressure-boundary & internals materials | SA-508 Gr.3 Cl.1 / SA-533B (RPV); ASTM A240 304/316L; Inconel-690 TT; Incoloy-800; reflector SA-965/SA-182 Type 304 | §8.4 / §8.3.6 |
| Fuel cladding | Zircaloy-4 (ASTM B811) | §8.3 |
| Reactor-core nuclear-design limits | IAEA SSG-52; NUREG-1431 Rev. 5 | peaking (F_Q, F_ΔH), coefficients, SDM (§8.2) |
| Neutronics method & data | OpenMC (Romano & Forget 2013); ENDF/B-VIII.0; ICSBEP / BEAVRS / C5G7 | §8.2, §8.13 |
| Decay heat | ANSI/ANS-5.1 | DHRS sizing, source term (§8.4, §8.11) |
| Water/steam properties | IAPWS-IF97 | §8.4, §8.9 |
| Radiation shielding / dose | ANSI/ANS-6.4; ICRP-116 | §8.2.6, §8.8 |
| Spent-fuel storage criticality | NUREG-0800 §9.1.1; 10 CFR 50.68 (k(95/95) ≤ 0.95) | §8.11 |
| Instrumentation & protection | IEEE Std 603; IEC 61513 / 60880; IAEA SSG-39 | §8.7 |
| Predisposal waste management | IAEA GSR Part 5 | §8.11 |
| Fire protection / H₂ safety | NFPA 2; IEC 60079 | §8.8, §8.10 |

8.1.8 Reference regulatory and nuclear-safety requirements

Nuclear safety is integrated from the outset by defence-in-depth: the four fundamental safety functions (reactivity control, fuel cooling, confinement, radiation protection) are each met by inherent characteristics plus independent, redundant provisions. The candidate site being in Türkiye, the licensing basis is the Nükleer Düzenleme Kurumu (NDK) framework (Nuclear Regulation Law No. 7381, 2022), whose design regulations adopt the IAEA Safety Standards.

Table 8.1-8

| Document | Scope | How addressed |
| --- | --- | --- |
| IAEA SSR-2/1 (Rev. 1) — Safety of NPPs: Design | Top-level design safety; defence-in-depth | Req. 24–25 redundant/independent reactivity control; Req. 35 (cogen isolation); Req. 45 inherent stability (coeffs < 0); Req. 46 ≥ 2 diverse shutdown systems; Req. 52–53 heat sink/grace (§8.2, §8.5, §8.6) |
| IAEA SSG-52 — Design of the Reactor Core | Core-design limits & methods | peaking, DNBR, coefficients, LHGR (§8.2) |
| IAEA GSR Part 4 (Rev.1) — Safety Assessment | Methodology | deterministic + projected-PSA (§8.5/§8.6) |
| IAEA SSG-3 / SSG-4 — L1 / L2 PSA | PSA methodology | CDF / LRF class targets (§8.6) |
| IAEA GSR Part 5 — Predisposal Waste Mgmt | Waste safety | on-site storage & conditioning (§8.11) |
| IAEA SSR-1; SSG-9 — Site Evaluation / external hazards | Siting | seismic, coastal hazard (§8.5, §8.10) |
| US NRC 10 CFR 50 App. A — GDC | Generic design criteria | GDC 11/26/27/35 (§8.2, §8.5, §8.6) |
| US NRC NUREG-1431 Rev. 5 — STS | LCO forms | SDM, MTC, F_Q, F_ΔH limits (§8.2) |
| US NRC NUREG-0800 / 10 CFR 50.68 | SRP; SFP criticality | k(95/95) ≤ 0.95 (§8.11) |
| Türkiye NDK — Law No. 7381 (2022) + NDK design regulation | National licensing | primary framework; adopts the IAEA standards above |

8.2. Core Design

The core structure of the modular reactor and all technical this structure should be presented in this section.

  - Material Selection: The materials to be used in the reactor core (such as fuel, cladding, coolant, moderator, and reflector) should be detailed together with the selection criteria. In addition, the behavior of these materials under neutron irradiation and within the operating temperature range (including steady-state conditions, transient conditions, and accident scenario temperatures) should be analyzed, and it should be demonstrated that they are suitable for the requirements of the designed reactor.

  - Geometry and Layout: It should be demonstrated that the reactor core has been designed according to the intended application, and the criteria and analyses related to the selection of the quantity, dimensions, and modeling parameters of the fuel elements, coolant, power control systems (control rods and/or burnable poison), neutron moderator, etc., should be presented.

  - Neutronic Analysis: As a result of the analyses, neutronic parameters such as criticality, neutron flux distribution, burnup distribution, feedback coefficients, and reactivity control values should be included in the report. The composition of all core components and their arrangement within the core (the neutronic design of the reactor core) should be provided through tables and figures. It should be demonstrated that the safety criteria adopted in the neutronic core design of the reactor comply with international and/or national regulations. The neutronic analyses are expected to be carried out from the beginning-of-cycle (BOC) to the equilibrium cycle.

  - Thermal-Hydraulic Analysis: The design should include a cooling system capable of removing the specified power generated from the core. The assumptions made during the steady-state thermal-hydraulic analyses forming the basis for the reactor core modeling, as well as the temperature distributions, pressure drops, and other thermal-hydraulic parameters obtained from the analyses, should be reported.

8.3. Fuel and Material Design

The design of the fuel and reactor structural materials used in the modular reactor, together with the related technical information, should be presented in this section.

  - The fuel performance efficiency and fuel safety studies for the fuel selected for the modular reactor design should be demonstrated through technical analyses and calculations.

  - The technical properties of the reactor structural materials to be used in the systems constituting the front-end fuel cycle should be explained.

8.4. Cooling Circuit System Design

Detailed information on all cooling systems used for the safe and high-performance cooling of the reactor core, as well as all components installed on these systems, together with analyses demonstrating the capacity of the cooling circuits, should be presented in this section.

  - A general description should be provided for the primary and secondary cooling systems used to cool the reactor, as well as the associated systems connected to them.

  - The functions, properties, capacities, and performance characteristics of the components in the cooling circuits (such as pumps, valves, pipes, heat exchangers, etc.) should be introduced in detail. It should be demonstrated that these components and their materials comply with the reactor safety criteria under all operating conditions.

  - The heat removal capacity of the cooling circuits should be demonstrated through analyses and methods accepted in the literature, and the operating conditions of the circuit should be defined.

8.5. Safety Criteria

Information regarding the safety criteria of the reactor should be presented in this section.

  - For the modular reactor, factors affecting the nuclear safety analysis—such as anticipated operational occurrences, criticality accidents, and design-basis accident scenarios—should be clearly specified. The modeling and analysis results for these scenarios should be reported and evaluated in detail.

  - The operating limit conditions of the designed reactor core and the calculations used to determine these conditions should be clearly stated.

  - The analysis results obtained regarding the safety criteria should demonstrate that the reactor has been designed to maintain its safety even under the worst possible scenarios.

  - It should be demonstrated that power control, cooling, and the prevention of fission product release are ensured under normal operating conditions, anticipated transient conditions, and accident conditions of the reactor.

8.6. Reactor Safety Systems Design

The reactor safety systems used to safely shut down the modular reactor, maintain it in a safe shutdown condition, and prevent the release of radioactive materials should be presented in this section.

  - All elements of the systems that provide safety functions against design-basis accidents, anticipated operational occurrences, criticality accidents, external events, and fault conditions—such as the reactor protection/shutdown system, heat removal system, emergency core cooling system, containment systems, and other safety systems—should be described in detail, and their functions should be explained.

  - The safety features should be designed and demonstrated in the report to automatically initiate the operation of appropriate systems, including reactivity control systems, to ensure that the specified acceptable fuel design limits are not exceeded as a result of anticipated operational occurrences, and to detect accident conditions and initiate the operation of systems and components important to safety.

  - The safety features should be designed and demonstrated in the report to transition the system into a safe state under conditions such as system disconnection, loss of energy (e.g., electrical power or instrument air), or assumed adverse environments (e.g., extreme heat or cold, fire, pressure, steam, water, and radiation).

  - The reactivity control systems should be designed within appropriate limits to ensure that the effects of assumed reactivity accidents do not result in damage to the reactor coolant pressure boundary or disturb the core, support structures, or other reactor pressure vessel internals in a manner that would significantly impair the core cooling capability, and this should be stated in the report.

  - For all possible conditions, risk analyses should be performed by constructing fault trees and event trees, and the results should be reported, including redundancy and requirement analyses of the safety systems.

  - It should be demonstrated with schematic diagrams how the parameters required to initiate reactor protective actions are derived from monitored variables such as neutron flux, temperature, and flow rate, and how these parameters are logically combined.

8.7. Instrumentation and Control System Design

  - Information regarding the design of the Nuclear Instrumentation and Control (I&C) system, which includes the functions required to manage the processes necessary to ensure adequate safety in modular reactors under normal operating conditions and accident conditions, should be presented in this section. These functions include the data and triggering mechanisms required to activate systems responsible for the mitigation of abnormal operating conditions and fault detection, the prevention or mitigation of accidents and their consequences within design limits, the prevention or mitigation of severe accidents and their consequences, and the mitigation of radiological consequences to the environment in the event of an accident.

  - The instrumentation and control system architecture of the reactor should be described in this section together with block diagrams, logic diagrams, and flow diagrams showing the main components, subsystems, and the connections between them. The sensors, detectors, and instruments to be used for data acquisition in the system, as well as the software and hardware required for real-time data processing, should be explained. The design of Human–Machine Interfaces (HMI) and secure communication protocols should also be specified.

  - The general design criteria and principles of the instrumentation and control system, the critical parameters that must be monitored and controlled, and the safety and operational requirements should be explained, taking into account factors such as redundancy, diversity, and physical separation.

  - It should be demonstrated that the main control room panel has been ergonomically designed.

8.8. Auxiliary Systems Design

Technical information regarding the auxiliary systems of the modular reactor (such as the ventilation system, electrical system, fire protection system, and radiation protection system) should be presented in this section.

  - All auxiliary systems, such as systems controlling the release of fission products, ventilation, compressed air, fuel handling and storage, and fire protection systems, should be clearly and comprehensively described under separate subsections. These descriptions should include the design purpose, operating principles, layout, safety functions (if any), performance characteristics, maintenance and repair requirements, etc., and should be supported by flow diagrams and instrumentation diagrams.

  - The on-site and off-site electrical systems supplying power to structures, systems, and components important to safety should be introduced together with their technical specifications, including emergency and uninterrupted power supplies, supported by graphs, drawings, and plans.

8.9. Energy Cycle and Integrated Systems

Technical information regarding the energy cycle of the modular reactor, including electricity generation and non-electrical applications, should be presented in this section.

  - The energy conversion system design and flow diagrams for electricity generation from the modular reactor should be provided.

  - Definitions and detailed analyses of the systems planned to be integrated with the modular reactor for non-electrical applications—such as hydrogen production, seawater desalination, district heating, and process heat facilities for industries—together with their connections to the plant, should be presented.

8.10. Plant Layout Design

An optimum general layout arrangement for the modular reactor, taking into account factors such as constructability, economic efficiency, safety, and operations, should be presented in this section.

  - The overall layout design of the modular reactor should be generally described, including the reactor building, energy conversion systems, operation and maintenance services, and other systems and buildings.

  - Two-dimensional and three-dimensional plans of the general layout design for the main buildings and structures should be provided together with explanations, showing the interconnections between all components. The plans, or the tables containing information forming the basis for the technical specifications of the plans, should also include information related to construction, such as main structures, steel structures, connection structures, weight distributions of the systems, and structural requirements.

  - During the planning process, the arrangement of critical piping within and between the structures, as well as their connections, should be clearly demonstrated. Critical piping refers to large-diameter lines carrying high-temperature fluids that directly affect the dimensions of the buildings and equipment layout, such as the main steam line, feedwater line, pressurizer lines, and decay heat removal lines.

8.11. Nuclear Waste Management

Studies aimed at reducing the quantity and radioactivity of nuclear waste generated from the modular reactor through an innovative nuclear fuel cycle design should be presented in this section.

  - The back-end stage of the fuel cycle, suitable for the modular reactor nuclear waste management solutions, should be explained in detail.

  - Analyses and calculations related to innovative waste management should be carried out in accordance with the criteria specified in Section 4.3.2 of the Technical Specification, and the results should be presented. In addition, this section should include evaluations regarding the compliance of the results with applicable regulations.

  - Furthermore, within the scope of waste management, design studies regarding the management of “secondary radioactive wastes” should also be presented here. Waste treatment processes should employ the best available techniques to prevent the generation of secondary radioactive waste through appropriate design and, where this is not possible, to minimize such waste in terms of both activity and quantity. Secondary wastes should be collected and segregated according to their nature, subsequent treatment, and/or intended destination; that is, wastes should not be mixed with other wastes having different characteristics that could subsequently compromise effective management or increase environmental impacts or risks.

8.12. Economic Evaluation

The economic advantages provided by the design should be discussed through comparisons with reference/similar reactors, and calculations related to investment, operation, and production costs should be presented.

REFERENCES

Reports must contain references. All the sources used must be properly cited under the references title. (E.g. Web sites, Book Names, Page Numbers)

APPENDICES

Additional documents, information, technical reports, technical drawings, etc. related to the design may be included under separate titles in this section in a way that does not disrupt the integrity of the report.

The Appendices section is not included in the page limit.

DIGITAL ATTACHMENTS: Digital data (sample input/output files, 3D technical drawings etc.) should be uploaded to the system in the form of a compressed zip/rar file, separate from the report.

The list of Digital Attachments should be provided in the Appendices section of this report (FER).

For all sections to be added to this part, cross-references (links) should be provided within the main report.

NOTES ON REPORT OUTLINE: (This page must be deleted before uploading the report.) - Final Evaluation Report (FER) must have maximum 120 pages except Cover Page, Contents, References and if needed Appendix. - All reports must be written according to academical standarts. - Every report must contain three seperate pages for “Cover Page, Content and References”. - Font: Arial, Size: 12, Title Font: Arial Black, Title Size: 14, Line Spacing: 1.15, All text must be justified, Page margins: must be set to 2.5 cm on all sides. - Sentences must not be repeated. - Teams must prepare the report according to provided template. Explanations in the template must be deleted. Subtitles must be used. E.g. Project Summary / Scope of the Project. - Report pages must be consecutively numbered. - Reports should not contain common knowledge and every information given must be cited properly. - Reference should be cited as: Digital Source: Author’s surname, Author’s Initials., Source Title, Publishing Date, Date of Access, URL. Published Source: Author’s surname, Author’s Initials., (Publising Date) Source Title, (If Applicable) Journal Name, (If Applicable) Journal Number, Page Number. - Final Evaluation Reports (FER) failing to comply with the provided template will not be evaluated.